## Slide 1
Training Module 3
Calculating the assessment
criteria of
SBTool – Building Scale

## Slide 2: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION | 
ISSUE | CATEGORY
B. Energy & Resource Consumption | B.1 Energy
RED: Renewable Energy Directive 2018/2001
New package of 8 different legislative proposals for
«Clean Energy for All Europeans package»
https://ec.europa.eu/energy/en/topics/energy-strategy-and-energy-union/clean-energy-all-europeans

## Slide 3: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
BACKGROUND (All RES for all uses)
EU Services Sector
EU Residential Sector
Source: Eurostat
RES
16%
Source: Eurostat
RES
3%

## Slide 4: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
BACKGROUND
Common practice
DHW: 1 m2 of flat plate collector per person
Space heating: 1 m2 of flat plate collector for a thermal load of 700 W
Domestic Hot Water (DHW)
Space Heating
Solar COMBI Systems
Solar Collectors
Heat Storage
Heat Distribution
Heat Dissipation
Auxiliary (backup)

## Slide 5: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
BACKGROUND
Common practice
Solar collector area: 3.6 m2/kWc
Auxiliary energy use: 0.255 kWhe/kWhc
Solar Collectors
Heat Storage
Heat Distribution
Heat-driven Cooling Unit
Cold Storage (optional)
Air Conditioning System
Cold Distribution
Auxiliary (backup)
+
COMBI-PLUS
Solar Cooling
DHW
Space Heating
Solar COMBI Systems

## Slide 6: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
Description | Unit | Project stage | Data source
Share of renewable energy in final thermal energy consumption | % | Design ____________ Occupancy | Estimation ____________ Metering
INDICATOR
Glazed flat plate
(60-90°C)
Evacuated tube
(80-120°C)
Unglazed
(25-50oC)
Concentrating
(95-160°C)
PV driven
Water source HP
(Closed loop)
PV driven
Ground source HP
(horizontal loop)
PV driven
Air source HP
(High SSER)
Wood pellets
Wood chips

## Slide 7: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
INTENT
Maximize the use of renewable energy sources.
Solar Combi Systems
Solar thermal for hot water production
(DHW + space heating)
Solar Combi Plus Systems
Solar thermal for chilled water production (cooling)
+ (DHW + space heating)
PV driven High efficiency heat pumps
Biomass
Ground source
Water source
Air source
Wood chips
Wood pellets
Ground source
Water source
Wood chips
Wood pellets

## Slide 8: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
This indicator assesses the share of renewable energy in final thermal energy consumption and thus, the degree to which renewable fuels have substituted fossil fuels and therefore contributed to the decarbonisation of the Mediterranean space economy.
It also quantifies the progress towards the Europe 2020 & 2030 targets for renewable energies.
DESCRIPTION

## Slide 9: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
BOUNDARY & SCOPE
The assessment boundary is the building.
The scope of the indicator includes the following energy uses, which are also referred to as technical building services:
heating,
cooling,
ventilation,
domestic hot water
The energy use is referred to as operational energy consumption.

## Slide 10: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
BOUNDARY & SCOPE
According to the Renewables Energy Directive (RED 2018), energy from renewable sources means energy from renewable non-fossil sources, namely wind, solar, aerothermal, geothermal, hydrothermal and ocean energy, hydropower, biomass, landfill gas, sewage treatment plant gas and biogases.
Heat pumps enabling the use of aerothermal, geothermal or hydrothermal heat at a useful temperature level need electricity or other auxiliary energy to function. The energy used to drive heat pumps should therefore be deducted from the total usable heat. Only heat pumps for which SPF > 1,15 * 1/η shall be taken into account.

## Slide 11: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
ASSESSMENT METHOD
The calculation method is provided by the CEN standards series that support implementation of the Energy Performance of Buildings Directive (EPBD) across the EU
The CEN standards series that currently forms the basis for most national calculation methods includes EN 15603 that collates the results from EN 13790
Simulations may provide accurate data
In case of existing buildings, the share of renewable energy in total final electric energy consumption should be evaluated by energy metering
Possible to use metered or estimated data for the energy use, so that it is feasible to populate this indicator
The source of data must always be clearly declared

## Slide 12: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
The actual thermal energy produced & used on-site from renewable sources (e.g. solar thermal collectors) can be monitored.
Use heat meters to measure delivered heat (e.g. from solar thermal collector array)
Measure the supply & return water flow temperature
Measure the supply & return water flow rate
Actual energy use data from at least 12 consecutive months is necessary.
It is preferable to average over longer records (e.g. three year data) in order to remove the effects of varying weather conditions and average out other inherent fluctuations in the building occupancy.
ASSESSMENT METHOD – GENERAL INFORMATION (Heat Meters)

## Slide 13: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
The actual thermal energy used on-site from biomass can also be calculated from the quantity of wood pellets or chips delivered to a building
Actual energy use data from at least 12 consecutive months is necessary.
It is preferable to average over longer records (e.g. three year data) in order to remove the effects of varying weather conditions and average out other inherent fluctuations in the building occupancy.
ASSESSMENT METHOD – GENERAL INFORMATION (Biomass Quantity)

## Slide 14: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
The actual thermal energy produced & used on-site from renewable sources or delivered to a building can be monitored. If available, BEMS or BMS can provide valuable data with a breakdown of the actual thermal energy use of the different technical installations.
Building energy management system (BEMS) control & monitor energy use of the various technical installations for heating, cooling, ventilation, lighting, plug loads etc, and indoor environmental conditions.
Building management system (BMS) may additionally include other functions (e.g. safety, access, lifts, fire security).
Actual energy use data from at least 12 consecutive months is necessary.
It is preferable to average over longer records (e.g. three year data) in order to remove the effects of varying weather conditions and average out other inherent fluctuations in the building occupancy.
ASSESSMENT METHOD – GENERAL INFORMATION (BEMS/BMS)

## Slide 15: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
ASSESSMENT METHOD - GENERAL INFORMATION
The annual thermal energy produced & used on-site from renewable sources is determined in relation to each energy carrier (fuel) that may replace.
For example,
Use solar thermal collectors to produce hot water that is then used for space heating instead of an oil-fired boiler.

## Slide 16: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
ASSESSMENT METHOD – DESIGN STAGE
The calculation steps new (design) buildings are the following:
Calculate the annual thermal energy produced & used on-site from renewable sources (e.g. solar collectors, PV driven HPs) to cover the demand for its technical services over a typical year, according to CEN standards that support EPBD, [kWh]

## Slide 17: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
ASSESSMENT METHOD – DESIGN STAGE
Calculate the annual thermal energy delivered (e.g. oil, natural gas, district heating) to the building to cover the demand of its technical services over a typical year, according to CEN standards that support EPBD, [kWh].
Sum the thermal energy from RES and the delivered thermal energy, to calculate the total final thermal energy (RES & conventional), [kWh]
Calculate the percentage ratio of the thermal energy produced from renewable sources to the total final thermal energy (RES & conventional), [%]
See also B.1.2 for design stage

## Slide 18: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
ASSESSMENT METHOD – OCCUPANCY STAGE
The calculation steps for existing buildings are the following:
Calculate the annual thermal energy produced & used on-site from renewable sources (e.g. solar collectors, PV driven HPs, biomass) to cover the demand for its technical services, using a 3year average value, from monitored data or calculations, [kWh]

## Slide 19: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
ASSESSMENT METHOD – OCCUPANCY STAGE
Calculate the annual thermal energy delivered (e.g. oil, natural gas, district heating) to the building to cover the demand of its technical services over a typical year according to CEN standards that support EPBD, [kWh]
Sum the thermal energy from RES and the delivered thermal energy, to calculate the total final thermal energy (RES & conventional), [kWh]
Calculate the percentage ratio of the thermal energy produced from renewable sources to the total final thermal energy (RES & conventional), [%]
See also B.1.2 for occupancy stage

## Slide 20: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
REFERENCES and STANDARDS
RED 2018. Directive (EU) 2018/2001 of the European Parliament and of the Council of 11 December 2018 on the promotion of the use of energy from renewable sources (recast). Brussels: European Commission. http://data.europa.eu/eli/dir/2018/2001/oj
2013/114/EU: Commission Decision of 1 March 2013
EN 15603:2008 - Energy performance of buildings. Overall energy use and definition of energy ratings. Brussels: European Committee for Standardization.
EN 13790:2008 - Energy performance of buildings. Calculation of energy use for space heating and cooling. Brussels: European Committee for Standardization.
Level(s) Part 1-2 – Beta version. Brussels: European Commission. https://environment.ec.europa.eu/topics/circular-economy/levels_en

## Slide 21: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
REFERENCES and STANDARDS
ASHRAE GreenGuide (5th ed.), Design, Construction and Operation of Sustainable Buildings, T. Lawrence, A.K. Darwich, J.K. Means, D. Macauley (Editors), 504 p., Atlanta: ASHRAE, 2018. https://www.ashrae.org/technical-resources/bookstore/ashrae-greenguide-the-design-construction-and-operation-of-sustainable-buildings
Handbook of Energy Efficiency in Buildings (1st ed.), Umberto Desideri and Francesco Asdrubali (Editors), 836 p., ISBN 978-0128128176, Butterworth-Heinemann, 2018. https://www.elsevier.com/books/handbook-of-energy-efficiency-in-buildings/desideri/978-0-12-812817-6
Solar Engineering of Thermal Processes (4th ed.), John A. Duffie, William A. Beckman, 944 p., ISBN: 978-0-470-87366-3, Wiley, 2013. https://www.wiley.com/en-us/Solar+Engineering+of+Thermal+Processes%2C+4th+Edition-p-9780470873663
Solar Cooling Handbook, A Guide to Solar Assisted Cooling and Dehumidification Processes, Hans-Martin Henning, Mario Motta, Daniel Mugnier (Editors), 368 p., ISBN 978-3990434383, Ambra Verlag, 2013.

## Slide 22: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
REFERENCES and STANDARDS
https://ec.europa.eu/energy/en/topics/energy-strategy-and-energy-union/clean-energy-all-europeans

## Slide 23: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
REFERENCES and STANDARDS
ASHRAE Standard 189.1 - Design of High-Performance Green Buildings. Source: https://www.ashrae.org/technical-resources/standards-and-guidelines/read-only-versions-of-ashrae-standards

## Slide 24: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
EXAMPLE - DESIGN STAGE

## Slide 25: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
A new office building is designed in Greece, served by a gas-fired central heating system. The small domestic hot water consumption of the building is served with solar thermal collectors.
Available data: The useful internal floor area is 2,995.8 m2. The calculated annual natural gas consumption for space heating is 13,278.1 m3. Solar thermal collectors cover 100% of the DHW demand. Simulations for the specific type of solar collectors, location, orientation etc, have provided an estimate of the annual thermal energy delivered to the building from renewables of 17,974.8 kWhth,RES
Calculate the percentage ratio of the amount of thermal energy produced from renewable sources to the total thermal energy.

## Slide 26: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
Calculate the energy content of the fuel (natural gas)
Quantity of Fuel: 13,278.1 m3
X
LHV Nat.gas (10.3 kWh/m3)
=
Delivered Thermal Energy
10.3 kWh/m3
136,764.4 kWhth,f
See B.1.2
Step 1
The calculated annual thermal energy delivered to the building from renewables is 17,974.8 kWhth,RES
Step 2

## Slide 27: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
154,739.2
Total thermal energy (fuels & RES ) (kWhth,t)
17,974.8
Thermal energy from RES (kWhth,RES)
=
______
11.6%
% RES Thermal
Step 4
Calculate the percentage ratio
Step 3
Calculate the total final thermal energy (RES & conventional)
17,974.8 kWhth,RES + 136,764.4 kWhth,f = 154,739.2 kWhth,t
x
100

## Slide 28: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
EXAMPLE - OCCUPANCY STAGE

## Slide 29: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
An existing office building in Athens is served by an oil-fired central heating system. In addition, a large solar thermal collector field is used to preheat the hot water for the hydronic central heating system used for space heating and cover the domestic hot water consumption of the building (solar combi system).
Available data: The building manager provided the annual fuel consumption from energy bills over several years (i.e. oil quantities that were delivered to the building) and the measured thermal energy produced from the solar collectors for the corresponding year.
Calculate the percentage ratio of the amount of thermal energy produced from renewable sources to the total thermal energy.

## Slide 30: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
 | 2015 | 2016 | 2017
Oil (lt) | 43,450 | 34,700 | 40,150
Thermal energy from RES (kWhth,RES) | 99,483 | 120,758 | 108,066
Annual quantity of fuel (oil) delivered to the building (lt) and thermal energy produced from solar collectors (kWhth,RES)
Available data

## Slide 31: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
Calculate the average annual thermal energy delivered
from the solar collectors for the technical building services
Calculate the three year average: kWhth,RES
Average annual thermal energy from RES: 109,436 kWhth,RES
Step 1
 | 2015 | 2016 | 2017
Thermal energy from RES (kWhth,RES) | 99,483 | 120,758 | 108,066

## Slide 32: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
Annual quantity of fuel (oil) delivered to the building
Used for space heating
Assume that the quantity of oil delivered to the building is actually used during the calendar year
Calculate the three year average: lt
Average annual quantity of fuel: 39,433 lt oil
 | 2015 | 2016 | 2017
Oil (lt) | 43,450 | 34,700 | 40,150
Step 2

## Slide 33: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
Calculate the energy content of the fuel (oil)
Quantity of Fuel: 39,433 lt
X
LHV Oil
(9.9 kWh/lt)
=
Delivered Thermal Energy
9.9 kWh/lt
390,386.7 kWhth,f
See B.1.2

## Slide 34: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
499,822.7
Total thermal energy (fuels & RES) (kWhth,f)
109,436
Thermal energy from RES (kWhth,RES)
______
21.9%
% RES Thermal
Step 4
Calculate the percentage ratio
Step 3
Calculate the total final thermal energy (RES & conventional)
109,436 kWhth,RES + 390,386.7 kWhth,f = 499,822.7 kWhth,t
=
x
100

## Slide 35: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
EXERCISE

## Slide 36: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
A new hospital building is designed that is served by a central HVAC system. It will be connected to central natural gas city network. The central HVAC system will be served by gas-fired boilers for space heating and domestic hot water.
The design team considers the installation of:
Central solar thermal collectors with hot water storage tanks to cover the domestic hot water demand and complement space heating
Available data: For the initial design, the calculated annual final thermal energy used by the technical building services in scope is 8,011MWhth,f over a typical year. For the alternative design, the calculated annual thermal energy produced from the solar combi system is 1,057MWhth,RES
Use the following data to solve the exercise
Calculate the percentage ratio of the amount of thermal energy produced from renewable sources to the delivered total thermal energy use.

## Slide 37: B.1.4 - ENERGY FROM RENEWABLE SOURCES IN TOTAL THERMAL ENERGY CONSUMPTION
Total = 8,011MWhth,f
Thermal energy consumption
Total = 1,057MWhth,RES
Available data
Thermal energy produced from the solar combi system