## Slide 1
Training Module 3
Calculating the assessment
criteria of
SBTool – Building Scale

## Slide 2: B.1.2 –THERMAL ENERGY CONSUMPTION
B.1.2 – THERMAL ENERGY CONSUMPTION | 
ISSUE | CATEGORY
B. Energy and Resource Consumption | B.1. Energy

## Slide 3: B.1.2 – THERMAL ENERGY CONSUMPTION
BACKGROUND
EU Services Sector
EU Residential Sector
Source: Eurostat
GAS
37%
OIL
12%
HEAT
8%
Source: Eurostat
GAS
31%
OIL
10%
HEAT
6%

## Slide 4: B.1.2 – THERMAL ENERGY CONSUMPTION
INDICATOR
Description | Unit | Project stage | Data source
Thermal energy consumption per internal useful floor area per year | kWh/m2/y | Design ____________ Occupancy | Estimation ____________ Metering

## Slide 5: B.1.2 – THERMAL ENERGY CONSUMPTION
INTENT
Minimize the total thermal energy consumption of the building.
District Heating
Heating Oil
Natural Gas
Liquefied petroleum gas
NZEB (EPBD 2018/844)
Nearly Zero Energy Buildings
All new buildings from 2021
Public new buildings from 2019
Clean Energy for All Europeans
New package of measures for providing the stable legislative framework needed to facilitate the clean energy transition towards the creation of the Energy Union
https://ec.europa.eu/energy/en/topics/energy-strategy-and-energy-union/clean-energy-all-europeans

## Slide 6: B.1.2 – THERMAL ENERGY CONSUMPTION
DESCRIPTION
The indicator provides an understanding of a building's thermal energy consumption.
This is in general responsible for the majority of life cycle energy use for buildings constructed before 2000.
Thermal energy is delivered to the building in the form of district heat/cold and fuel. It is the energy per 'carrier' supplied to the building, to satisfy uses within the building (heating, cooling, ventilation, domestic hot water). The ‘delivered energy’ is the one metered by the utilities.

## Slide 7: B.1.2 – THERMAL ENERGY CONSUMPTION
BOUNDARY & SCOPE
The assessment boundary is the building.
The scope of the indicator includes the following energy uses, which are also referred to as technical building services:
heating,
cooling,
ventilation,
domestic hot water
The energy use is referred to as operational energy consumption.

## Slide 8: B.1.2 – THERMAL ENERGY CONSUMPTION
BOUNDARY & SCOPE
The actual fuel quantities delivered to a building can be monitored. If available, BEMS or BMS can provide valuable data with a breakdown of the actual thermal energy use of the different technical installations.
Building energy management system (BEMS) control & monitor energy use of the various technical installations for heating, cooling, ventilation, lighting, plug loads etc, and indoor environmental conditions.
Building management system (BMS) may additionally include other functions (e.g. safety, access, lifts, fire security).
Actual energy use data from at least 12 consecutive months is necessary.
It is preferable to average over longer records (e.g. three year data) in order to remove the effects of varying weather conditions and average out other inherent fluctuations in the building occupancy.

## Slide 9: B.1.2 – THERMAL ENERGY CONSUMPTION
BOUNDARY & SCOPE
The actual annual fuel delivered to a building is also available from bills or utilities. Average over longer periods (e.g. 3year records).
The main challenge for gas consumption is that the breakdown for the different building technical services and other end-uses (e.g. cooking) is not evident.
Desegregation for different end-uses is facilitated by BEMS, if available for buildings in operation, calibrated building simulations, or establish a base line (e.g. monitor gas consumption that is used for cooking in summer.

## Slide 10: B.1.2 – THERMAL ENERGY CONSUMPTION
ASSESSMENT METHOD
The calculation method is provided by the CEN standards series that support implementation of EPBD across the EU
The CEN standards series that currently form the basis for most of national calculation methods includes EN 15603 that collates the results from EN ISO 13790
Possible to use metered or estimated data for the energy use, so that it is feasible to populate this indicator
The source of data must always be clearly declared

## Slide 11: B.1.2 – THERMAL ENERGY CONSUMPTION
ASSESSMENT METHOD
Can use most national calculation methods that are aligned with the EN standards and are being used for
Building performance assessment or
Issuing Energy Performance Certificates (EPCs)

## Slide 12: B.1.2 – THERMAL ENERGY CONSUMPTION
The calculation steps for new (design) buildings are the following:
Calculate the annual total thermal energy delivered to the building over a typical year, in the form of district heat/cold or/and fuel, to cover the demand of its technical services, [kWh]
ASSESSMENT METHOD – DESIGN STAGE
Calculate the internal useful floor area of the building,[m2]
Calculate the indicator’s value as: total thermal energy use of the building (step 1) / total useful internal floor area (step 2), [kWh/m2/y]

## Slide 13: B.1.2 – THERMAL ENERGY CONSUMPTION
The calculation steps for existing buildings are the following:
Calculate the annual quantity of each fuel (e.g. liters of oil, cubic meters of natural gas) delivered to the building for its technical services or the heat/cold from district networks, using a 3year average value
ASSESSMENT METHOD – OCCUPANCY STAGE (Fuels)
Metered data from
Monitoring
Measure all quantities of fuel delivered to the building and provide measured energy consumption data from at least 12 consecutive months
Provides the best quality data
or

## Slide 14: B.1.2 – THERMAL ENERGY CONSUMPTION
Source: ASHRAE Standard 100: 2018. Energy Efficiency in Existing Buildings. Atlanta: ASHRAE.
Heating Oil
where A = measured inventory of fuel at the beginning of the 12 month period; B = the quantity of fuel delivered to the building during the 12 month period; C = measured inventory of fuel at the end of the 12 month period
ASSESSMENT METHOD – OCCUPANCY STAGE (Fuels)
The main challenge for fuels delivered in bulk to a building for storage prior to actual use (e.g. oil, solid fuels), the annual quantity of fuel for that energy carrier is estimated as follows:
Quantity of Fuel = A + B – C
Bills / Utilities
Average over longer periods (e.g. 3year records)

## Slide 15: B.1.2 – THERMAL ENERGY CONSUMPTION
Convert the amount of each fuel to thermal energy using their lower heating values, [kWh]
Sum the thermal energy of all fuels to calculate the total thermal energy use of the building, [kWh]
Calculate the internal useful floor area of the building, [m2]
Calculate the indicator’s value as: total thermal energy use of the building (step 3) / total useful internal floor area (step 4), [kWh/m2/y]
ASSESSMENT METHOD – OCCUPANCY STAGE (Fuels)

## Slide 16: B.1.2 – THERMAL ENERGY CONSUMPTION
ASSESSMENT METHOD – OCCUPANCY STAGE (District Heat/Cold)
The calculation steps for existing buildings are the following:
Calculate the annual total thermal energy delivered to the building from a district heating system (or cold), [kWh]
Typically measured at the building
Calculate the internal useful floor area of the building, [m2]
Calculate the indicator’s value as: total thermal energy use of the building (step 1) / total useful internal floor area (step 2), [kWh/m2/y]

## Slide 17: B.1.2 – THERMAL ENERGY CONSUMPTION
EPBD:2018 - Energy Performance of Buildings Directive, 2018/844/EU. Brussels: European Parliament and the Council of the European Union.
EN 15603:2008 - Energy performance of buildings. Overall energy use and definition of energy ratings. Brussels: European Committee for Standardization.
EN 13790:2008 - Energy performance of buildings. Calculation of energy use for space heating and cooling. Brussels: European Committee for Standardization.
Level(s) Part 1-2 – Beta version. Brussels: European Commission. https://environment.ec.europa.eu/topics/circular-economy/levels_en
REFERENCES and STANDARDS

## Slide 18: B.1.2 – THERMAL ENERGY CONSUMPTION
REFERENCES and STANDARDS
https://ec.europa.eu/energy/en/topics/energy-strategy-and-energy-union/clean-energy-all-europeans

## Slide 19: B.1.2 – THERMAL ENERGY CONSUMPTION
EXAMPLE - DESIGN STAGE

## Slide 20: B.1.2 – THERMAL ENERGY CONSUMPTION
A new office building is designed in Greece, served by a gas-fired central heating system. Domestic hot water is served with local electric continuous-flow (tankless) water heaters.
Available data: The useful internal floor area is 2,995.8 m2. The calculated annual natural gas consumption is 13,278.1 m3
Calculate the thermal energy consumption per building’s useful internal floor area per year (i.e. final thermal energy use intensity).

## Slide 21: B.1.2 – THERMAL ENERGY CONSUMPTION
Calculate the energy content of the fuel (natural gas)
Quantity of Fuel: 13,278.1 m3
X
LHV Nat.gas (10.3 kWh/m3)
=
Delivered Thermal Energy
10.3 kWh/m3
136,764.4 kWhth
Step 1
Step 2
The building’s useful internal floor area is 2,995.8 m2

## Slide 22: B.1.2 – THERMAL ENERGY CONSUMPTION
Calculate the annual thermal energy use intensity (kWh/m2/y)
136,764.4 kWhth

=
Delivered Thermal Energy
2995.8 m2
45.6 kWhth/m2/y
Useful internal
floor area (m2)
Step 3

## Slide 23: B.1.2 – THERMAL ENERGY CONSUMPTION
EXAMPLE - OCCUPANCY STAGE

## Slide 24: B.1.2 – THERMAL ENERGY CONSUMPTION
An existing office building located in Athens is served by an oil-fired central heating system. Domestic hot water is served with local electric continuous-flow (tankless) water heaters.
Available data: The building manager provided the floor plans and annual fuel consumption from energy bills over several years. The oil quantities correspond to the total fuel orders that were delivered to the building during the corresponding year.
Calculate the thermal energy consumption per building’s useful internal floor area per year (i.e. final thermal energy use intensity).

## Slide 25: B.1.2 – THERMAL ENERGY CONSUMPTION
 | 2015 | 2016 | 2017
Oil (lt) | 50,500 | 43,900 | 48,100
Annual quantity of fuel (oil) delivered to the building
Typical floor plan
Floor plans have been verified during a short energy audit of the building and can be used to estimate the building’s useful floor area
Available data

## Slide 26: B.1.2 – THERMAL ENERGY CONSUMPTION
Annual quantity of fuel (oil) delivered to the building
Assume that the quantity of oil delivered to the building is actually used during the calendar year for the technical services
Calculate the three year average: lt
Average annual quantity of fuel: 47,500 lt oil used for space heating
 | 2015 | 2016 | 2017
Oil (lt) | 50,500 | 43,900 | 48,100
Step 1

## Slide 27: B.1.2 – THERMAL ENERGY CONSUMPTION
Calculate the energy content of the fuel (oil)
Quantity of Fuel: 47,500 lt
X
LHV Oil
(9.9 kWh/lt)
=
Delivered Thermal Energy
9.9 kWh/lt
470,250 kWhth
Steps 2 - 3

## Slide 28: B.1.2 – THERMAL ENERGY CONSUMPTION
Calculate the building’s useful floor area
Use the available floor plans that have been reviewed and confirmed to comply with the existing building during a short energy audit.
Use internal dimensions
Useful internal floor area: 4,915.1 m2
Typical floor
Step 4

## Slide 29: B.1.2 – THERMAL ENERGY CONSUMPTION
Calculate the annual thermal energy use intensity (kWhth/m2/y)
470,250 kWhth

=
Delivered Thermal Energy
4915.1 m2
95.7 kWhth/m2/y
Useful internal
floor area (m2)
Step 5

## Slide 30: B.1.2 – THERMAL ENERGY CONSUMPTION
EXERCISE

## Slide 31: B.1.2 – THERMAL ENERGY CONSUMPTION
A building located in Athens is served by a gas-fired central heating system. Domestic hot water is served with local electric continuous-flow (tankless) water heaters.
Available data: The building manager provided the floor plans and annual fuel consumption from energy bills over several years. The quantities of natural gas correspond to the total fuel delivered to the building during the corresponding year.
Use the following data to solve the exercise
Calculate the thermal energy consumption per building’s useful internal floor area per year (i.e. final thermal energy use intensity).

## Slide 32: B.1.2 – THERMAL ENERGY CONSUMPTION
Floor Plans
Useful internal floor area = 416 m2
Available data

## Slide 33: B.1.2 – THERMAL ENERGY CONSUMPTION
Natural Gas Consumption (m3)
 | Month | 2015 | 2016 | 2017
 | January | 686.9 | 809.5 | 959.9
 | February | 713.0 | 868.5 | 1019.0
 | March | 545.1 | 750.0 | 868.5
 | April | 211.1 | 300.6 | 217.7
 | May | 0.0 | 0.0 | 0.0
 | June | 0.0 | 0.0 | 0.0
 | July | 0.0 | 0.0 | 0.0
 | August | 0.0 | 0.0 | 0.0
 | September | 0.0 | 0.0 | 0.0
 | October | 41.1 | 463.4 | 86.4
 | November | 311.4 | 551.8 | 201.9
 | December | 718.2 | 930.7 | 566.1
Available data