## Slide 1
Training Module 3
Calculating the assessment
criteria of
SBTool – Building Scale

## Slide 2: D1.7 – MECHANICAL VENTILATION
D1.7 – MECHANICAL VENTILATION | 
ISSUE | CATEGORY
D. Indoor Environmental Quality | D.1 Indoor Air Quality and Ventilation

## Slide 3: D1.7 – MECHANICAL VENTILATION
INDICATOR
Description | Unit | Project stage | Data source
Mechanical ventilation rate per useful internal floor area | l/s/m2 | Design ____________ Occupancy | Estimation ____________ Measurements
Only for buildings with mechanical ventilation systems

## Slide 4: D1.7 – MECHANICAL VENTILATION
INTENT
Ensure an effective air exchange rate facilitating high indoor air quality and sufficient indoor thermal comfort conditions

## Slide 5: D1.7 – MECHANICAL VENTILATION
DESCRIPTION
This indicator measures the number of times every hour that new air from outside enters a room and is mixed and exchanged with old air from inside.
Low air change rate results to trapped allergens, pollutants and irritants that can degrade the indoor air quality and affect the well-being of occupants
High air change rate results to thermal discomfort and energy waste

## Slide 6
BOUNDARY & SCOPE
The assessment boundary is the building’s useful conditioned space.
For an occupied building, the measurements are performed in all spaces with characteristic functions of the building (e.g. office spaces, meeting room, cafeteria), different orientations (e.g. on the side of a façade facing the street), and floors (e.g. first, middle and last floor). The indicator value for the building is then calculated as a weighted average of the corresponding measurements.
For the design phase, the indicator must be calculated for all mechanical ventilation systems in the building. The indicator value for the building is then calculated as a weighted average of the corresponding estimated or measured values.
D1.7 – MECHANICAL VENTILATION

## Slide 7
ASSESSMENT METHOD – DESIGN STAGE
A design simulation of the building's ventilation strategy in accordance with EN 16798-7 should be used to calculate the ventilation rate.
D1.7 – MECHANICAL VENTILATION

## Slide 8
ASSESSMENT METHOD – OCCUPANCY STAGE
The ventilation rate shall be tested as part of the commissioning process on site according to the methods described in Annex D of EN 12599.
The average ventilation rate shall be reported.
Measurements can be taken at a number of points in a system.
The measurements shall be made for the related ducts and/or air terminals that supply air to the internal spaces as identified according to the guidance in section 2.1.2.2 of the reference standard.
D1.7 – MECHANICAL VENTILATION

## Slide 9
ASSESSMENT METHOD – OCCUPANCY STAGE
The calculation steps are the following:
Calculate the mechanical ventilation rate in each selected characteristic space, [l /s]
Calculate the internal floor area of each characteristic space, [m2]
Calculate the mechanical ventilation rate per internal floor area in each selected characteristic space, [l /s/m2]
Calculate the total internal floor area of all selected characteristic spaces, [m2]
Sum the products of the mechanical ventilation rate in each characteristic space multiplied by the corresponding floor area
D1.7 – MECHANICAL VENTILATION

## Slide 10
ASSESSMENT METHOD – OCCUPANCY STAGE
Calculate the weighted value of the mechanical ventilation rate for the building as the ratio of the sum of products of the ventilation rate (step 4) to the total internal floor area of the selected characteristic spaces (step 3), [l/s/m2].
D1.7 – MECHANICAL VENTILATION
Ventilation Rate
where
Vi = Ventilation rate calculated in the i-th room (l/s/m2)
Su,i = useful floor area of the i-th room (m2)
l/s/m2

## Slide 11
REFERENCES and STANDARDS
Level(s) (the European framework for sustainable buildings) indicator 4.1: Indoor air quality. Document developed by European Commission - Joint Research Centre, January 2021
EN 16516: construction products: Assessment of release of dangerous substances - Determination of emissions into indoor air
ISO 16000-6:2021 - Indoor air — Part 6: Determination of organic compounds (VVOC, VOC, SVOC) in indoor and test chamber air by active sampling on sorbent tubes, thermal desorption and gas chromatography using MS or MS FID
EN 16798-1: 2019 Energy performance of buildings - Ventilation for buildings - Part 1: Indoor environmental input parameters for design and assessment of energy performance of buildings addressing indoor air quality, thermal environment, lighting and acoustics.
EN 16798-7:2017. Energy performance of buildings - Ventilation for buildings - Part 7: Calculation methods for the determination of air flow rates in buildings including infiltration. Brussels: European Committee for Standardization.
EN 12599 - Ventilation for buildings - Test procedures and measurement methods to hand over air conditioning and ventilation systems.
D1.7 – MECHANICAL VENTILATION

## Slide 12
EXAMPLE
D1.7 – MECHANICAL VENTILATION

## Slide 13: D1.7 – MECHANICAL VENTILATION
An existing small office building has the following spaces:
Office space 1: floor area 65m2 and ventilation rate 31.9 l/s
Office space 2: floor area 15m2 and ventilation rate 14 l/s
Office space 3: floor area 15m2 and ventilation rate 7 l/s
Conference room : floor area 30m2 and ventilation rate 56.2 l/s
Circulation spaces : floor area 35m2 and ventilation rate 11 l/s
Toilets : floor area 10m2 and ventilation rate 6 l/s
Calculate the ventilation rate per useful internal floor area
Steps 1 - 2

## Slide 14: D1.7 – MECHANICAL VENTILATION
Step 5
Sum the products of the mechanical ventilation rate in each space multiplied by the corresponding floor area
((0.49 *65) + (0.93 *15) + (0.47 *15) + (1.87 *30)) = 109,1 l/s
Step 3
Step 4
Calculate the total internal floor area of all selected spaces: 125 m2
Calculate the mechanical ventilation rate per internal floor area in the selected characteristic spaces excluding circulation spaces and service rooms (i.e. toilets):
Office space 1: 0.49 l/s/ m2
Office space 2: 0.93 l/s/ m2
Office space 3: 0.47 l/s/ m2
Conference room : 1.87 l/s/ m2

## Slide 15
D1.7 – MECHANICAL VENTILATION
Step 6
Calculate the average ventilation rate per useful internal floor area
125 (m2)
109.1 l/s)
=
______

## Slide 16
EXERCISE
D1.7 – MECHANICAL VENTILATION

## Slide 17: D1.7 – MECHANICAL VENTILATION
A new small dwelling is designed with the following spaces:
Circulation space: 10m2; ventilation rate of 6L/S
Living Room and Kitchen: 30m2; ventilation rate 7L/s
Bedroom 1: 13m2; ventilation rate 9.1 L/s
Bedroom 2: 15m2; ventilation rate 8L/s
Toilets: 6m2; ventilation rate 5L/s
Calculate the ventilation rate per useful internal floor area