## Slide 1
Training Module 3
Calculating the assessment
criteria of
SBTool – Building Scale

## Slide 2: D.2.3 - THERMAL COMFORT INDEX
D.2.3 – THERMAL COMFORT INDEX | 
ISSUE | CATEGORY
D. Indoor Environmental Quality | D.2 Air Temperature & Relative Humidity

## Slide 3: D.2.3 - THERMAL COMFORT INDEX
BACKGROUND
A human being's thermal sensation is mainly related to the thermal balance of the body as a whole
Thermal comfort responds to the interaction of various parameters
Physical (e.g. air temperature & humidity, mean radiant temperature, air speed)
Personal (e.g. physical activity, clothing)
Organic (e.g. age, sex, national characteristics of occupants)

## Slide 4: D.2.3 - THERMAL COMFORT INDEX
The thermal comfort indices Predicted Mean Vote (PMV) and Predicted Percentage Dissatisfied (PPD), allow to predict the general thermal sensation and degree of discomfort (thermal dissatisfaction) of people exposed to moderate thermal environments.
They enable the analytical determination and interpretation of indoor thermal comfort, giving the environmental conditions considered acceptable for general thermal comfort as well as those representing local discomfort.
BACKGROUND
Source IPCC
PMV scale

## Slide 5: D.2.3 - THERMAL COMFORT INDEX
BACKGROUND
Factors that can cause local thermal discomfort
The sensation of thermal comfort or discomfort is in practice more complex than defining an upper & lower temperature range, or considering the human body as a whole.
Issues to consider:
Draughts
Vertical air temperature differences
Floor temperature
Radiant temperature asymmetry

## Slide 6: D.2.3 - THERMAL COMFORT INDEX
Description | Unit | Project stage | Data source
Predicted Percentage of Dissatisfied (PPD) | % | Design ____________ Occupancy | Estimation ____________ Measurement
INDICATOR

## Slide 7: D.2.3 - THERMAL COMFORT INDEX
INTENT
Facilitate the assessment of indoor thermal comfort conditions

## Slide 8: D.2.3 - THERMAL COMFORT INDEX
BOUNDARY & SCOPE
The assessment boundary is the building.
Calculations are performed in all spaces with characteristic functions of the building (e.g. office spaces, meeting room, cafeteria), different orientations (e.g. on the side of a façade facing the street), and floors (e.g. first, middle and last floor). Calculations are also performed in spaces where the most extreme values of the thermal parameters are observed or anticipated (e.g. occupied areas near windows, diffuser outlets, corners, entries). The indicator value for the building is then calculated as a weighted average of the corresponding measurements

## Slide 9: D.2.3 - THERMAL COMFORT INDEX
BOUNDARY & SCOPE
The indicator is calculated for summer or winter periods considering different prevailing conditions, clothing etc. This is based on the main priorities in terms of thermal discomfort conditions during summer or winter.
The time period (summer or winter) considered in the calculations must be clearly stated and considered during the analysis.

## Slide 10: D.2.3 - THERMAL COMFORT INDEX
ASSESSMENT METHOD
The PPD value is estimated or measured in accordance to EN 16798 both in summer and winter conditions. The approach is following along the lines of the ASHRAE Standard 55.

## Slide 11: D.2.3 - THERMAL COMFORT INDEX
The calculation steps are the following:
Estimate or Measure PMV in each selected space *
Calculate PPD in each selected space, [%] *
Calculate the internal floor area of each space, [m2]
Calculate the total internal floor area of the selected spaces, [m2]
Sum the PPD in each space multiplied by the corresponding area to calculate the weighted PPD
Calculate the indicator’s value as the ratio of the weighted PPD (step 5) to the total internal floor area (step 4), [%]
ASSESSMENT METHOD
%

## Slide 12: D.2.3 - THERMAL COMFORT INDEX
* Calculation steps 1 and 2 :
Estimate PMV for spaces in buildings under design, using the indoor thermal conditions, occupants’ clothing and metabolic rate (activity) as expected for the use of the indoor spaces
For mechanically conditioned spaces the design conditions (e.g. air temperature, humidity, speed) are set for acceptable indoor comfort
For naturally ventilated spaces (no mechanical cooling) need to estimate indoor conditions
ASSESSMENT METHOD – DESIGN STAGE
Thermal comfort ZONE

## Slide 13: D.2.3 - THERMAL COMFORT INDEX
Estimate PMV in a selected space
Select the design air temperature (dry bulb-db) and relative humidity for the main space functione.g. for offices 26(20)oC and 45(35)% in summer(winter)
Select the design indoor air speed, e.g. 0.15 m/s
Calculate the mean radiant temperature of indoor wall surfaces (oC)
ASSESSMENT METHOD – DESIGN STAGE
Mechanically conditioned buildings
Mean radiant temperature (mrt) is a key variable in making thermal calculations for the human body. It is the uniform temperature of an imaginary enclosure in which radiant heat transfer from the human body equals the radiant heat transfer in the actual non-uniform enclosure. The radiant temperature is the temperature of an exposed surface in the environment. The temperatures of individual surfaces are usually combined into a mean radiant temperature. The mrt can also be calculated from the temperature of the surrounding walls and surfaces and their positions with respect to the person.

## Slide 14: D.2.3 - THERMAL COMFORT INDEX
Determine the main physical activity of the occupants (related to the metabolic rate), e.g. seated office work (1 met)
Determine the typical type of clothing ensembles, e.g. light indoor summer clothing (0.5 clo)
Calculate the PMV using the equation described in EN ISO 7730
ASSESSMENT METHOD – DESIGN STAGE (Mechanically conditioned)
Metabolic Rates for Typical Activities (ASHRAE)
Typical Clothing Ensembles (ASHRAE )

## Slide 15: D.2.3 - THERMAL COMFORT INDEX
Estimate PPD.
PPD = 100 – 95  exp[-(0.03353  PMV4 + 0.2179  PMV2)]
Several computer codes are available that predict PMV & PPD
e.g. ASHRAE Thermal Comfort Tool
Online tool http://comfort.cbe.berkeley.edu
ASSESSMENT METHOD – DESIGN STAGE (Mechanically conditioned)
Acceptable thermal environmental conditions for general comfort:
0.5  PMV  0.5 and
PPD  10%

## Slide 16: D.2.3 - THERMAL COMFORT INDEX
Calculate the running mean of outdoor temperature (Trm)
Trm =
where Tod is the daily mean outdoor temperature for the previous day (Tod-1), the day before (Tod-2) and so on
ASSESSMENT METHOD – DESIGN STAGE
Naturally ventilated buildings
Calculate the Operative temperature (To)
Allowable To room temperature for buildings used for human occupancy with mainly sedentary activities (1 to 1.3met), with easy access to operable windows and occupants may freely adapt their clothing to the indoor and/or outdoor thermal conditions
Acceptable indoor temperatures

## Slide 17: D.2.3 - THERMAL COMFORT INDEX
Operative temperature (To) is the uniform temperature of an imaginary black enclosure, and the air within it, in which an occupant would exchange the same amount of heat by radiation plus convection as in the actual non-uniform environment
The maximum number of occupants feel that the indoor temperature is acceptable (PMV = 0)
ASSESSMENT METHOD – DESIGN STAGE (Naturally conditioned)
Examples of recommended design values (EN 16798-1)

## Slide 18: D.2.3 - THERMAL COMFORT INDEX
Acceptable indoor temperatures (Adaptive method) as Operative Temp (To)
ASSESSMENT METHOD – DESIGN STAGE (naturally ventilated)
In landscaped (open plan) offices occupants have limited access to operable windows and therefore poor control over natural ventilation. Therefore, the temperature limits may not always apply in such situations
Increased indoor air speed may be used to compensate for increased operative temperatures (To)
Lower clothing, activity, mean radiant temperature, expand comfort zone to higher To
Verify the thermal comfort category and the associated PPD

## Slide 19: D.2.3 - THERMAL COMFORT INDEX
ASSESSMENT METHOD – OCCUPANCY STAGE
Measure the PPD in a selected space.
Use a PMV/PPD meter to record indoor conditions and predict the prevailing thermal comfort conditions
or
Measure independently the indoor environmental conditions (i.e. air temperature and relative humidity, globe temperature*, air speed) and calculate PMV & PPD
* Globe temperature can be measured directly; it is a good approximation of the operative temperature and is also used with other measurements to calculate the mean radiant temperature (mrt)

## Slide 20: D.2.3 - THERMAL COMFORT INDEX
ASSESSMENT METHOD – OCCUPANCY STAGE
Thermal environment measurements are made in the building at a representative sample of locations, i.e.
The center of the room or space
1m inward from the center of each of the room’s walls and if there are windows, the measurements are taken 1m inward from the center of the largest window
Measurements are also taken in locations where the most extreme values of the thermal parameters are observed or anticipated (e.g. occupied areas near windows, diffuser outlets, corners, entries)
Measurement periods cover several hours, representative of total occupancy (e.g. season, typical day)

## Slide 21: D.2.3 - THERMAL COMFORT INDEX
REFERENCES and STANDARDS
EN ISO 7730 – Ergonomics of the thermal environment – Analytical determination and interpretation of thermal comfort using calculation of the PMV and PPD indices and local thermal comfort criteria
EN 16798-1:2017 - Energy performance of buildings - Part 1: Indoor environmental input parameters for design and assessment of energy performance of buildings addressing indoor air quality, thermal environment, lighting and acoustics - Module M1-6 (revision of EN 15251). Brussels: European Committee for Standardization.
Level(s) Part 1-2 – Beta version. Brussels: European Commission. https://environment.ec.europa.eu/topics/circular-economy/levels_en
ASHRAE Standard 55:2017 - Thermal Environmental Conditions for Human Occupancy. Atlanta: ASHRAE.

## Slide 22: D.2.3 - THERMAL COMFORT INDEX
EXAMPLE - DESIGN STAGE

## Slide 23: D.2.3 - THERMAL COMFORT INDEX
Design indoor conditions in two spaces with different occupant activities are listed on the floor plan of an office building:
Temperature db (oC)
Relative humidity (%)
Air speed (m/s)
Mean radiant temperature (oC)
Occupant activity (met)
Clothing ensembles
Available data
Calculate the PPD for the building
12 m2
15 m2

## Slide 24: D.2.3 - THERMAL COMFORT INDEX
http://comfort.cbe.berkeley.edu
Space 1
Space 2
Steps 1 - 2
Calculate the PPD for each space

## Slide 25: D.2.3 - THERMAL COMFORT INDEX
Step 5
Sum the products of the PPD in each space multiplied by the corresponding floor area
((6 *12) + (19 *15)) = 357 % m2
Step 3
Step 4
Calculate the total internal floor area of all selected spaces: 27 m2
The internal floor area for each space is :
Space 1: 12 m2 Space 2: 15 m2
Step 6
Calculate the average PPD
=
27 (m2)
357 (% m2)
______

## Slide 26: D.2.3 - THERMAL COMFORT INDEX
EXAMPLE - OCCUPANCY STAGE

## Slide 27: D.2.3 - THERMAL COMFORT INDEX
Indoor conditions in two spaces with different occupant activities were measured over five-day period, in an office building:
Temperature db (oC)
Relative humidity (%)
Air speed (0.15 m/s)
Mean radiant temperature (oC)
Occupant activity (#1 Seated office work-1 met); #2 Filling, standing-1.4 met)
Clothing ensembles (Light indoor summer clothing-0.5 clo)
Calculate the PPD for the building

## Slide 28: D.2.3 - THERMAL COMFORT INDEX
Space #1 (20m2)
Space #2 (12m2)
Steps 1 - 2

## Slide 29: D.2.3 - THERMAL COMFORT INDEX
Step 5
Sum the products of the PPD in each space multiplied by the corresponding floor area
((6 *12) + (19 *15)) = 393 % m2
Step 3
Step 4
Calculate the total internal floor area of all selected spaces: 32 m2
The internal floor area for each space is :
Space 1: 20 m2 Space 2: 12 m2
Step 6
Calculate the average PPD
=
32 (m2)
393 (% m2)
______

## Slide 30
EXERCISE

## Slide 31: D.2.3 - THERMAL COMFORT INDEX
Indoor conditions in one space were measured in an office building:
Temperature db (oC) 19
Relative humidity (%) 40
Air speed (m/s) 0.1
Mean radiant temperature (oC) assume db+2oC
Occupant activity Reading, seated
Clothing ensembles Typical business suit (winter indoor clothing)
Input data to solve the exercise
http://comfort.cbe.berkeley.edu/
Calculate the PPD for the building