## Slide 1
Training Module 3
The assessment criteria of
SBTool – Building Scale

## Slide 2: E.1.2 – SMART READINESS INDICATOR
E.1.2 – SMART READINESS INDICATOR (SRI) | 
ISSUE | CATEGORY
E. Service Quality | E.3 Controllability

## Slide 3: E.1.2 – SMART READINESS INDICATOR
BACKGROUND
Smart buildings & IoT
Adapted from Plageras et al. 2018. https://doi.org/10.1016/j.future.2017.09.082
Use of automation, controls and electronic monitoring in technical building systems and operations
Advances of internet of things (IoT) greatly enhance the ability to handle big data by monitoring, processing, storing and analysing information from different building functions, equipment and operating conditions

## Slide 4: E.1.2 – SMART READINESS INDICATOR
BACKGROUND
Main features of smart buildings :
Automation in order to facilitate the automatic operation of equipment and appliances or perform automatic functions
Multi-functionality in order to allow for multiple functions
Adaptability in order to learn, predict and satisfy the needs of occupants and minimize the loads from the outdoor environment
Interactivity in order to allow the interaction and data exchange among occupants and installations
Efficiency in order to improve performance, reduce operating cost and save time

## Slide 5: E.1.2 – SMART READINESS INDICATOR
BACKGROUND
The SRI concept was adopted by the energy performance of buildings directive [1] and further strengthened by the subsequent legal acts [2-3] that establish the SRI as an official EU instrument.
SRI has evolved and matured to a common EU rating scheme for evaluating the smartness of buildings
Currently an optional scheme. However, the proposed EPBD revision adopted in 2021 foresees further strengthening the SRI.

## Slide 6: E.1.2 – SMART READINESS INDICATOR
Description | Unit | Project stage | Data source
Total smart readiness of buildings for responding to the needs of occupants, optimizing energy performance, and interacting with energy grids | % | Design ____________ Occupancy | Estimation ____________ Estimation
INDICATOR

## Slide 7: E.1.2 – SMART READINESS INDICATOR
INTENT
Reach more energy efficient, environmentally friendly, healthy and comfortable indoor environments.
Assesses how smart a building is in terms of:
Responding to the needs of the occupant (e.g. health, comfort, well-being, etc.)
Using energy efficient control strategies
Interacting with energy grids (energy flexibility / demand response and system integration)

## Slide 8: E.1.2 – SMART READINESS INDICATOR
INTENT
Use smart technologies in buildings as a cost-effective way to
Create healthier & more comfortable buildings
Lower energy use & carbon emissions
Digital technologies, e.g. smart thermostats, lighting controls, can have a short pay back (within 2 years)
Smart technologies, e.g. automated shading controls or ventilation control based on measurements using air-quality sensors, can improve health, well-being and comfort
Intelligent scheduling of energy use (e.g. operating white appliances, charging electric vehicles) can result in significant energy savings, and also contribute to grid balancing

## Slide 9: E.1.2 – SMART READINESS INDICATOR
DESCRIPTION
A common EU scheme for rating the smart readiness of buildings
SRI assesses how smart a building is in terms of:
1. Responding to the needs of the occupant (e.g. health, comfort, well-being, etc.)
2. Using energy efficient control strategies
3. Interacting with energy grids (energy flexibility / demand response and system integration)

## Slide 10: E.1.2 – SMART READINESS INDICATOR
The assessment boundary is the building.
The scope of the indicator includes the following energy uses, which are also referred to as technical building services (domains):
heating
cooling
ventilation,
domestic hot water
lighting
dynamic building envelope
electricity
electric vehicle charging
monitoring and control
BOUNDARY & SCOPE

## Slide 11: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
Assess the smart-ready services that the building or building unit has or could use from a service catalogue (Verbeke et al. 2020) that are grouped into 9 major building services (domains)

## Slide 12: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
Assess buildings or building units based on their capacity to satisfy 3 major building functionalities:
1 – Optimize energy efficiency and overall in-use performance
2 – Adapt their operation to the needs of the occupant
3 – Adapt to signals from the grid (energy flexibility)

## Slide 13: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
Assess the smart-readiness functionalities into 7 impact criteria:
Energy efficiency
Maintenance and fault prediction
Comfort
Convenience
Health, Well-being and accessibility
Information to occupants
Energy flexibility and storage

## Slide 14: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
Aggregate the outcome of the assessment in an SRI score that quantifies the various building or building unit characteristics and functions in relation to a maximum smart readiness

## Slide 15: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
Default weighting factors are all equally allocated for the calculation of the final score according to relative importance of each domain and relevance.
Each functionality is equally weighted by one third in the calculation of the SRI score
Each impact criteria is equally weighted for the calculation of the score for each functionality
Each major building service (domain) is equally weighted under an impact criteria
The optimized energy functionality contributes by 33.3% to the overall SRI score, while each one of the two impacts (energy efficiency and maintenance/fault) will contribute by 16.7% each for the calculation of the SRI score

## Slide 16: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
The SRI score is the ratio of the impact scores from the assessed smart ready services to the maximum obtainable score (the sum of all impacts in case all smart services are implemented at the highest functionality level)
100% Building that has the highest currently possible level of smartness
0% Building that has no smartness
Detailed scores by building service (domain) and imp[act criterion
(upto 57 scores)
Aggregated scores for each technical building services
(upto 9 scores)
Aggregated scores for each of the 7 impact criteria
Aggregated scores for each of the 3 functionalities
Overall SRI score & SRI class
(seven classes, from SRI < 20% to SRI > 90%)

## Slide 17: E.1.2 – SMART READINESS INDICATOR
Method A – Simplified (low complexity buildings, i.e. existing residential or small non-residential buildings)
Use a simplified service catalogue (Verbeke et al. 2020) with only 27 pre-defined services
Use a check-list
Complete assessment in less than an hour
Suitable for a self-assessment of a building
Method B – Detailed (high complexity buildings, i.e. new buildings and non-residential buildings)
Use with a detailed service catalogue (Verbeke et al. 2020) with 54 pre-defined services
On-site inspection and walk-through audit
Complete in about a day
Need an expert and engage building’s facility manager
ASSESSMENT METHOD
Two assessment methods that focus on qualitative approaches of various building services based on an expert assessment

## Slide 18: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
Predefined services at different functionality levels for heating, domestic hot water, cooling (SRI calculation sheet-Method A)

## Slide 19: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
Predefined services at different functionality levels for lighting, dynamic building envelope, electricity, EV, and miscellaneous (SRI calculation sheet-Method A)

## Slide 20: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
Examples of predefined services at different functionality levels for heating and domestic hot water (SRI calculation sheet-Method B)

## Slide 21: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
Each smart-ready service that is present in a building is assessed and the functionality level is determined according to the various features included in the predefined catalogue. For each smart readiness impact criterion, the individual score I(d,ic) of each major building service (domain) is determined, as follows:
))
where, d is the number of the major building service (domain) under assessment, ic is the number of the impact criterion under consideration, Nd is the total number of the different functions in a technical domain d, Si,d is function i of technical domain d, FL(Si,d) is the functionality level of function Si,d as available in the building or building unit, Iic(FL(Si,d)) is the score of function Si,d for impact criterion number ic, according to the service’s functionality level.
In accordance with the predefined catalogue of smart-ready functions, the maximum score of each technical domain for each impact criterion Imax(d,ic) is determined, as follows:
))
where, FLmax(Si,d) is the highest functionality level that function Si,d could have according to the smart-ready service catalogue, Iic(FLmax(Si,d)) is the score of function Si,d for its highest functionality level, which means the maximum score of function Si,d for impact criterion number ic.

## Slide 22: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
The smart readiness score is calculated as a percentage for each of the impact criterion SRic using the weighting factors as follows:
where, d is the number of the major building service (domain) under assessment, N is the total number of technical domains, Wd,ic is the weighting factor expressed as a percentage of the major building service number d for impact criterion number ic.
The smart readiness scores along the three major building functionalities are determined using the corresponding weighting factors, as follows:
where, M is the total number of impact criteria, Wf(ic) is the weighting factor expressed in percentage of impact criterion number ic for key functionality f, SRic is the smart readiness score for impact criterion number ic.

## Slide 23: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD
The total smart readiness score is calculated as a weighted sum of the key functionalities’ smart readiness scores, as follows:
where, SRf is the smart readiness score for key functionality f, Wf is the weight of key functionality f in the calculation of the total smart readiness scores, with ΣWf = 1.

## Slide 24: E.1.2 – SMART READINESS INDICATOR
ASSESSMENT METHOD – Simplified (Existing) & Detailed (New)
The calculations are performed using a Calculation Sheet that is available with the Service Catalogue, a Practical Guide in the SRI Assessment Package and are available on request from the dedicated SRI website
https://energy.ec.europa.eu/topics/energy-efficiency/energy-efficient-buildings/smart-readiness-indicator/sri-explained_en#sri-methodology)
The assessment process is the same for both methods: Simplified (existing buildings) and Detailed (new buildings)
The service catalogue is different
Expertise required to conduct the assessment is different

## Slide 25: E.1.2 – SMART READINESS INDICATOR
[1] EPBD:2018 - Energy Performance of Buildings Directive, 2018/844/EU. Brussels: European Parliament and the Council of the European Union. https://eur-lex.europa.eu/eli/dir/2018/844/oj
[2] Commission Delegated Regulation (EU) 2020/2155 of 14 October 2020 supplementing Directive (EU) 2010/31/EU of the European Parliament and of the Council by establishing an optional common European Union scheme for rating the smart readiness of buildings, Brussels. http://data.europa.eu/eli/reg_del/2020/2155/oj
[3] Commission Implementing Regulation (EU) 2020/2156 of 14 October 2020 detailing the technical modalities for the effective implementation of an optional common Union scheme for rating the smart readiness of buildings, Brussels. http://data.europa.eu/eli/reg_impl/2020/2156/oj
[4] The Smart Readiness Indicator (SRI) for rating smart readiness of the European building stock, SRI Factsheet, European Commission. https://energy.ec.europa.eu/system/files/2022-04/SRI-Factsheet-v6_0.pdf
REFERENCES and STANDARDS

## Slide 26: E.1.2 – SMART READINESS INDICATOR
REFERENCES and STANDARDS
Smart readiness indicator – SRI, European Commission. https://energy.ec.europa.eu/topics/energy-efficiency/energy-efficient-buildings/smart-readiness-indicator_en
SRI Explained, European Commission. https://energy.ec.europa.eu/topics/energy-efficiency/energy-efficient-buildings/smart-readiness-indicator/sri-explained_en

## Slide 27: E.1.2 – SMART READINESS INDICATOR
EXAMPLE – SIMPLIFIED & DEATAILED METHODS

## Slide 28: E.1.2 – SMART READINESS INDICATOR
An existing office building in Athens, Greece is designed with a central HVAC system that is served by variable refrigerant flow (VRF) heat pumps. Electricity is the only energy carrier used in the building. The building is not equipped with any on-site renewables for electricity generation, nor electric vehicle charging, which are not mandated by code.
Available data: The useful internal floor area is 2995.8 m2. The building was constructed in the 50s and renovated in the late 90s.
Obtain the SRI Assessment Package and use the SRI calculation sheet that is available with the service catalogue and practical guide
Calculate the smart readiness indicator – SRI using both methods (A and B)

## Slide 29: E.1.2 – SMART READINESS INDICATOR
Step 1
BUILDING INFORMATION

## Slide 30: E.1.2 – SMART READINESS INDICATOR
Step 1
BUILDING INFORMATION

## Slide 31: E.1.2 – SMART READINESS INDICATOR
Step 2
CALCULATION SHEET
Method A
27 pre-defined services

## Slide 32: E.1.2 – SMART READINESS INDICATOR
Step 2
CALCULATION SHEET
Method B
54 pre-defined services

## Slide 33: E.1.2 – SMART READINESS INDICATOR
Step 3
WEIGHTING
Use default weightings

## Slide 34: E.1.2 – SMART READINESS INDICATOR
Results - Method A
Results - Method B
Step 4
RESULTS

## Slide 35: E.1.2 – SMART READINESS INDICATOR
EXERCISE

## Slide 36: E.1.2 – SMART READINESS INDICATOR
Consider an existing, standalone, naturally ventilated house located in suburban Athens, with a useful internal floor area of 325 m2. The building was constructed in the 90s. The building is not equipped with on-site renewables for electricity generation, nor electric vehicle charging, which are not mandated by code.
Obtain the SRI Assessment Package and use the SRI calculation sheet that is available with the service catalogue and practical guide
Use the following data to solve the exercise
Calculate the smart readiness indicator – SRI using both methods (A and B)

## Slide 37: E.1.2 – SMART READINESS INDICATOR
Available data