## Slide 1
Training Module 4
Calculating the assessment
criteria of
SNTool – Neighbourhood Scale

## Slide 2: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS | 
ISSUE | CATEGORY
B. Energy | B.2. Energy Consumption
See also Β.1.2 of Building Scale

## Slide 3
BACKGROUND
EU Services Sector
EU Residential Sector
Source: Eurostat
GAS
37%
OIL
12%
HEAT
8%
Source: Eurostat
GAS
31%
OIL
10%
HEAT
6%

## Slide 4: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
4
BACKGROUND
Thermal energy is delivered to the building in the form of fuel (e.g. natural gas, fuel oil, LPG, logs, pellets, chipped wood or other fuels) and district heat/cold. It is the energy per 'carrier' supplied to the building, to satisfy uses within the building (heating, cooling, ventilation, domestic hot water). The ‘delivered energy’ is the one metered by the utilities.

## Slide 5: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
INDICATOR
Indicator | Unit | Data source
Aggregated annual total final thermal energy consumption per aggregated indoor useful floor area | kWh/m2/year | Metered or estimated data
For the evaluation of the actual performance of the urban area it is preferable to use metered data.
If metered data aren’t available, estimated data shall be used.
Estimated data are used for evaluating retrofit scenarios in planning and decision-making processes
The source of data must always be clearly declared.

## Slide 6: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
INTENT
Estimate and minimize thermal energy consumption for all buildings in the neighbourhood.

## Slide 7: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
7
DESCRIPTION
The indicator provides an understanding of the final thermal energy consumption for all the existing buildings in the neighborhood
Use stage energy consumptions are in general responsible for the majority of life cycle energy use in the case of buildings constructed before the turn of the millennium.
NATURAL GAS
for space heating and domestic hot water
NATURAL GAS for cooling
FUEL OIL
for space heating and domestic hot water
Fuel oil boilers Natural gas condensing boilers Natural gas absorption chiller

## Slide 8: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
ASSESSMENT METHOD
The calculation method is provided by the CEN standards series that support implementation of EPBD across the EU
The CEN standards series that currently forms the basis for most of national calculation methods includes EN 15603 that collates the results from EN ISO 13790

## Slide 9: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
In the calculation of the final thermal energy consumption, the following energy uses should be considered:
heating
cooling
mechanical ventilation
domestic hot water
BOUNDARY & SCOPE
The assessment boundary includes all buildings in the neighbourhood.
Energy use is referred to as operational energy consumption

## Slide 10: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
The calculation steps are the following:
For each building in the neighborhood collect actual data of each fuel (e.g. liters of oil, cubic meters of natural gas) or the heat/cold from district networks, for the energy uses taken into account
ASSESSMENT METHOD – USE OF METERED DATA
Collected data for final non-renewable thermal energy consumption, from:
Monitoring (Provides the best quality data)
Measure all quantities of fuel delivered to the building and provide measured energy consumption data from at least 12 consecutive months
Bills or Utilities
Average over longer periods (e.g. 3year records)
Highly recommended assessment method!
For each building in the neighborhood calculate the average annual consumption per fuel or district heat/cold, for the energy uses taken into account

## Slide 11: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
ASSESSMENT METHOD – USE OF METERED DATA
Highly recommended assessment method!
For each building in the neighborhood calculate the indoor useful area, in square meters [m2]
Data available from energy performance certificate, energy audit report, building/usage permit or other documentation of a building
Sum the annual fuel (or heat/cold from district networks) of each building up to an aggregated total annual consumption per fuel or district heat/cold
Convert the amount of fuels to thermal energy consumption using their lower heating values

## Slide 12: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
Sum the average annual thermal energy of all fuels up to an aggregated total annual final thermal energy consumption [kWhth/year]
Sum the indoor useful area of each building in the area up to an aggregated total indoor useful area, in square meters [m2]
Calculate the indicator’s value as: aggregated annual total final thermal energy consumption (step 6) / aggregated indoor useful area (step 7), [kWhth/m2/year]
ASSESSMENT METHOD – USE OF METERED DATA

## Slide 13: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
The calculation steps are the following:
For each building in the neighborhood calculate the annual thermal energy consumption for the energy uses taken into account, in kilowatt hours, [kWhth/year].
ASSESSMENT METHOD – USE OF ESTIMATED DATA
Annual energy for space heating and cooling should be assessed for actual climatic data and actual building use, using the quasi-steady state monthly method, according to the EN 13790 (Energy performance of buildings – Calculation of energy use for space heating and cooling).
Annual energy for domestic hot water should be assessed according to the EN 15316-3-1 (Domestic hot water systems, characterisation of needs (tapping requirements))
The fuels may be used for combustion (e.g. use oil or natural gas for space heating) or CHP to generate useful heat

## Slide 14: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
For each building in the neighborhood calculate the indoor useful area, in square meters, [m2]
Sum the annual final thermal energy consumption of each building up to an aggregated total annual final thermal energy consumption, [kWhth/year]
Sum the indoor useful area of each building in the area up to an aggregated total indoor useful area, in square meters, [m2]
Calculate the indicator’s value as: aggregated annual total final thermal energy consumption (step 3) / aggregated indoor useful area (step 4), [kWhth/m2/year]
ASSESSMENT METHOD – USE OF ESTIMATED DATA

## Slide 15: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
COMPLEX METHOD – calculations of annual final thermal energy are based on the set of norms EN 151316 (Heating systems in buildings – Method for calculation of system energy requirements and system efficiencies)  it is recommended to use appropriate calculation software tool!
SIMPLIFIED METHOD – calculations of annual final thermal energy are based on assumed efficiency values for main subsystems of heating/domestic hot water/cooling systems (distribution subsystem, generation subsystem)
Suitable software tool required!
Notes: MARINA
which norm will be used depends on the configuration of building-integrated heating/domestic hot water/cooling system

## Slide 16: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
COMPLEX METHOD - set of norms EN 15316:
EN 15316-2-1 Space heating emission systems
EN 15316-2-3 Space heating distribution systems
EN 15316-3-1 Domestic hot water systems, characterisation of needs EN 15316-3-2 Domestic hot water systems, distribution
EN 15316-3-3 Domestic hot water systems, generation
EN 15316-4-1 Space heating generation systems, combustion systems (boilers)
EN 15316-4-2 Space heating generation systems, heat pump systems
EN 15316-4-3 Space heating generation systems, thermal solar systems
EN 15316-4-4 Space heating generation systems, building-integrated cogeneration systems
EN 15316-4-5 Space heating generation systems, the performance and quality of district heating and large volume systems
EN 15316-4-7 Space heating generation systems, biomass combustion systems
Suitable software tool required!
Notes: MARINA

## Slide 17: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
SIMPLIFIED METHOD - set of norms EN 15316:
1
2
3
 GENERATION SUBSYSTEM
 DISTRIBUTION SUBSYSTEM
 EMISSION SUBSYSTEM
1
2
3
boiler  dis  reg = total
boiler  boiler efficiency
dis  efficiency of distribution subsystem
reg  efficiency of control system
total  total heating system efficiency
HEATING SYSTEM with boiler as a heat source
Total final thermal energy for space heating:
Regulation system | ηreg [%]
Central automatic | 95
Manual regulation – constant control | 92
Manual regulation – periodical control | 90
Notes: MARINA

## Slide 18: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
REFERENCES and STANDARDS
EPBD:2018 - Energy Performance of Buildings Directive, 2018/844/EU. Brussels: European Parliament and the Council of the European Union
EN ISO 13790 Energy performance of buildings – Calculation of energy use for space heating and cooling
EN 15316-2-1 Space heating emission systems
EN 15316-2-3 Space heating distribution systems
EN 15316-3-1 Domestic hot water systems, characterisation of needs
EN 15316-3-2 Domestic hot water systems, distribution
EN 15316-3-3 Domestic hot water systems, generation
EN 15316-4-1 Space heating generation systems, combustion systems (boilers)
EN 15316-4-2 Space heating generation systems, heat pump systems
EN 15316-4-3 Space heating generation systems, thermal solar systems
Notes: MARINA

## Slide 19: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
REFERENCES and STANDARDS
EN 15316-4-4 Space heating generation systems, building-integrated cogeneration systems
EN 15316-4-5 Space heating generation systems, the performance and quality of district heating and large volume systems
EN 15316-4-7 Space heating generation systems, biomass combustion systems
EN 15603 Energy performance of buildings – Overall energy use and definition of energy ratings
Level(s) Part 1-2 – Beta version. Brussels: European Commission
https://environment.ec.europa.eu/topics/circular-economy/levels_en
Notes: MARINA

## Slide 20: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
REFERENCES and STANDARDS
https://ec.europa.eu/energy/en/topics/energy-strategy-and-energy-union/clean-energy-all-europeans

## Slide 21: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
EXAMPLE

## Slide 22: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
In an existing neighborhood, there are 5 small residential buildings, 15 single houses, one office building and one junior school. All buildings are connected to the main electricity grid and most of them to the central natural gas network.
Available data: The useful internal floor area and the calculated annual thermal energy consumption of all buildings in the neighborhood
Calculate the annual total final thermal energy consumption per total
useful internal floor area (i.e. final thermal energy use intensity).

## Slide 23: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
For single houses and residential buildings the internal floor area and the annual thermal energy consumption are given as a total aggreggated value for all the buildings within the category
Available data
 | Useful internal floor area (m2) | Calculated annual thermal energy consumption (kWhth) | HVAC systems (heating, cooling, domestic hot water)
Office | 1045 |  | Central HP for heating, cooling and domestic hot water.
School | 1847 | 59452 | Central natural gas boiler for space heating. Local HP for space cooling. Electric heaters for domestic hot water.
Single houses (15) | 1805 | 202521 | Central natural gas boiler for space heating and domestic hot water. Local HP for space cooling.
Residential buildings (5) | 3322 | 291007 | Central natural gas boiler for space heating and domestic hot water. Local HP for space cooling
Steps 1 -2

## Slide 24: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
Step 3
Calculate the total annual final thermal energy consumption for all the buildings in the neighborhood
(0+59452+202521+291007) = 552980 kWhth
Step 4
Calculate the total indoor useful floor area for all the buildings in the neighborhood
(1045+1847+1805+3322) = 8109 m2
Step 5
Calculate the annual total final thermal energy consumption per total useful internal floor area
Total Indoor Useful Floor Area
552980 kWhθ

=
Total Thermal energy
8109 m2
68.2 kWhth/m2/y

## Slide 25: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
EXERCISE

## Slide 26: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
In an existing neighborhood, there are 22 single houses, one kindergarten and one junior school. All buildings are connected to the main electricity grid and all of them are equipped with central boilers (natural gas or fuel oil).
Available data: The useful internal floor area and the calculated annual thermal energy consumption of all buildings in the neighborhood
Calculate the annual total final thermal energy consumption per total
useful internal floor area (i.e. final thermal energy use intensity).

## Slide 27: B.2.1 – TOTAL FINAL THERMAL ENERGY CONSUMPTION FOR BUILDING OPERATIONS
Available data
 | Useful internal floor area (m2) | Calculated annual thermal energy consumption (kWhth) | HVAC systems (heating, cooling, domestic hot water)
Kindergarten | 456 | 52470 (fuel oil ) | Central fuel oil boiler for space heating. Local HP for space cooling. Electric heaters for domestic hot water.
School | 2151 | 112929 (natural gas) | Central natural gas boiler for space heating. Local HP for space cooling. Electric heaters for domestic hot water
Single houses (22) | 2530 | 311443 (natural gas) | Central natural gas boiler for space heating and domestic hot water. Local HP for space cooling.
For single houses the internal floor area and the annual thermal energy consumption are given as a total aggreggated value for all the buildings